Cooling Tower Risk Management Plan Template

Components and Format of a Risk Management Plan (RMP)

A RMP should have a number of basic components that would include:

- Site and key contact details.

- Assessment of each of the critical risks.

- Attachments or reference to other documents such as operational manuals and plans, maintenance plans, shut-down procedures, etc.

There is no prescribed format for an RMP - this Template is provided as a guide - other formats can be used as long as they contain all of the information required by this Template.

About the Template

The Template is to be completed by Cooling Tower operators which includes the owner or the person in control of the Cooling Tower(s).  Hamilton Public Health Services staff created this Template and it has been adapted by the Middlesex-London Health Unit with their permission, based on a review of the current ASHRAE and CTI Guidelines for Legionella control in Cooling Towers, new draft ASHRAE Standards for prevention of Legionella in building systems (Standard 188), and the Risk Management Plan Template developed by the Health Protection Branch of the Victorian State Government, Department of Health, Australia.

Completing this Template or creating your RMP in another format will meet the requirement of having a RMP.

A RMP must be developed for every Cooling Tower on the site. The RMP, once developed, must be made available to a Public Health Inspector on request.

The Template is also available in Word format at www.healthunit.com/risk-management-plans-cooling-tower-systems and can be modified to develop your RMP.

Disclaimer

This Template is intended only as a general guide to the development of Risk Management Plans for Cooling Towers. No warranty as to the completeness of the information is given. The Middlesex-London Health Unit and its employees disclaim all liability and responsibility for any direct or indirect loss or damage which may be suffered through reliance on any information contained in or omitted from this Template, and no person should act solely on the basis of the information contained in the Template without taking appropriate professional advice about obligations in specific circumstances.

# Site and Key Contact Details

| Record | Your details |
| --- | --- |
| Site location (property address) |  |
| Number of Cooling Towers |  |
| Cooling Tower(s)Registration Number |  |
| Cooling Tower(s) location reference (If one exists) |  |
| Property owner’s name/contact details (Include corporation name, if applicable, and contact person’s business and after-hours telephone numbers) |  |
| Cooling Tower(s)owner’s name/contact details (Include corporation name, if applicable, and contact person’s business and after-hours telephone numbers) |  |
| Who is responsible for day-to-day operation of the Cooling Tower(s)? (Include corporation name, if applicable, and contact person’s business and after-hours telephone numbers). This person must have authority to approve the disinfection of the Cooling Tower(s) on request of Middlesex-London Health Unit. This person is not the water treatment service provider. |  |
| Water treatment provider name/contact details (Include corporation name, if applicable, and contact person’s business and after hours telephone numbers) |  |

# Critical Risks

## Stagnant Water

| Stagnant Water Risk Control Strategy | Assessment of Cooling Tower(s) (Tick box) | Improvement Response - Indicate the improvements that will be put in place | Proposed Completion Date | Date Completed |
| --- | --- | --- | --- | --- |
| Cooling Tower(s) shutdown and start up procedures | Is a Cooling Tower (or part of a Cooling Tower) idle for more than three days? □ Yes - if Yes, answer question immediately below. □ No | Not Applicable | N/A | N/A |
|  | Is there a start up procedure to ensure stagnant water is either drained to waste or treated with a biocide regimen prior to Cooling Tower start up? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Removal or activation of any ‘dead legs’ | Are there ‘dead legs’ in the Cooling Tower(s)? □ Yes - if Yes describe how you will address this risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. □ No; proceed to next section below. |  |  | Date Name Signature |

## Nutrient Growth

| Nutrient Growth Risk Control Strategy | Assessment of the Cooling Tower(s) | Improvement Response - Indicate the improvements that will be put in place | Proposed Completion Date | Date Completed |
| --- | --- | --- | --- | --- |
| Identify and manage sources of organic contamination | Are there sources of organic material or debris near the Cooling Tower(s) that could contaminate the Cooling Tower(s) and increase the level of nutrients? Sources of organic material are; dust from nearby construction, road dust, birds, (nesting, faeces, carrion) leaves, etc. □ Yes - if Yes, please note the source and type of organic material and describe how this risk will be reduced or managed in the response column. Also; assign a proposed completion date; and date and sign when the improvement is completed. □ No; proceed to next section below. |  |  | Date Name Signature |
| Control corrosion | Is a corrosion control program in place? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Scaling Control | Is a scaling control program in place? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Sediment Control | Is a sediment control program in place? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Cleaning and Disinfection | Is/Are the Cooling Tower(s) cleaned and disinfected prior to initial start–up and after any shut down period greater than three days? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Protect the basin and ‘top deck’ of the Cooling Tower(s) from sunlight | Are any of the wetted surfaces exposed to sunlight? □ Yes if Yes; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. □ No; proceed to next section below. |  |  | Date Name Signature |

## Water Quality

| Water Quality Risk Control Strategy | Assessment of the Cooling Tower(s) | Improvement Response - Indicate the improvements that will be put in place | Proposed Completion Date | Date Completed |
| --- | --- | --- | --- | --- |
| Water treatment program | Are two or more biocides used in a one week rotation? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
|  | Is a compatible bio-dispersant used in a water treatment program? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
|  | Are control measures in place that measure and confirm that the water chemistry is under control? □ Yes; Describe these in the response column □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Testing for HPC | Is the recirculation water tested for HPC? □ Yes □ No |  |  | Date Name Signature |
| Testing for Legionella | Is the recirculation water tested for Legionella? □Yes □ No | N/A; testing for Legionella is not a requirement, however, PHS is interested in knowing which Cooling Towers in London are being tested for Legionella. |  |  |
| Response to the detection of Legionella | How would you respond to Legionella being detected in a sample? □ According to ASHRAE recommendations □ According to CTI recommendations □ According to Cooling Tower manufacturer instructions □ Other response(describe in response column) |  |  | Date Name Signature |
| Labelling of Cooling Tower(s) | Is/Are the Cooling Tower(s) labelled with the Cooling Tower(s) Registration Number (CT ID)? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Automated biocide dosing device | Is an automated biocide dosing device installed? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Automated dosing devices for all chemicals or agents | Are automated dosing devices for all chemicals/agents installed? □Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Appropriate location for chemical dosing | Is the chemical dosing location well away from where the sampling point for bacterial tests? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Provision of a dedicated water testing location | Is the water chemistry always tested at the same location? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Labelling of water testing location | Is the water testing location clearly labelled? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risk in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |

## 4. Maintenance and Operations

| Cooling Tower Maintenance Strategy | Assessment of the Cooling Tower(s) | Improvement Response - Indicate the improvements that will be put in place | Proposed Completion Date | Date Completed |
| --- | --- | --- | --- | --- |
| Review the maintenance program against ASHRAE, CTI, manufacturer’s instructions or recommendations | What documents were used as a guide for a maintenance program review? □ ASHRAE □ CTI □ Manufacturer’s instructions or recommendations □ Other organization’s document (describe in response column) □ None;- if None; describe how you will address the risk in the response column |  |  | Date Name Signature |
|  | Has a maintenance review been conducted? □ Yes; proceed to next section below. □ No - if No; describe how you will address this in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
|  | Are there any improvements that can be made to the maintenance program? □ Yes - if Yes; describe the improvements in the response column; assign a proposed completion date; and date and sign when the improvement is completed. □ No; proceed to next section below. |  |  | Date Name Signature |
| Operating and maintenance manuals | Are operating and maintenance manuals developed? □ Yes; proceed to next section below. □ No - if No; describe how you will address the risks in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
| Age of the Cooling Tower(s) | When was/were the Cooling Tower(s) built? |  |  |  |
| Drift eliminator | Are drift eliminators fitted to the Cooling Tower(s)? □ Yes; proceed to next section below. □ No; if No; describe how you will address the risks of excessive drift leaving the Cooling Tower(s) in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |
|  | Are the drift eliminators in good condition (i.e. no holes found and they are not worn-out or clogged). □ Yes; proceed to next section below. □ No – if No; describe how you will address the risks of excessive drift leaving the Cooling Tower(s) in the response column; assign a proposed completion date; and date and sign when the improvement is completed. |  |  | Date Name Signature |

## 5. Location and Access

| Location and Access Risk Control Strategy | Assessment of the Cooling Tower(s) | Improvement Response | Proposed Completion Date | Date Completed |
| --- | --- | --- | --- | --- |
| Understand the extent of potential exposure to the Cooling Tower(s) | Is/Are the Cooling Tower(s) located in a hospital or a long term care facility (nursing home, retirement home, home for the aged)? □ Yes □ No If No above, is/are the Cooling Tower(s) located within 500m of a hospital or a long term care facility (nursing home, retirement home, home for the aged)? □ Yes; please name the facility(s) within 500 metres in the response column □ No |  | Not Applicable | Not Applicable |

# 6.	Communication

|  | Details |  |  |
| --- | --- | --- | --- |
| List names and contact details of who you will inform in the event of a positive Legionella test | Category | Name/Title | Telephone |
|  | Staff |  |  |
|  | Occupational Health Staff/Contractors |  |  |
|  | Unions |  |  |
|  | Building Owner |  |  |
|  | Other Building Tenants |  |  |
|  | Corporation Spokesperson |  |  |
|  | Chief Executive |  |  |
|  | Public Health Services | Environmental Health | 519-663-5317 ext. 2300 |
|  | Other |  |  |

# Endorsement of Risk Management Plan

| Name/position of person responsible for Risk Management Plan |  |
| --- | --- |
| Signature |  |

This appears on the Certificate of Registration supplied by Middlesex-London Health Unit. The Cooling Tower ID will be issued once the cooling tower is registered.

Other response plan must incorporate the minimum recommendations by ASHRAE or CTI.

The Cooling Tower(s) should be labelled the Registration Number or CT ID that is provided by Middlesex-London Health Unit once the cooling tower is registered.